## Annual 24h Outage
Inputs and Assumptions
RIE Customers Served by Nasonville Substation | 4670
CREW Customers Served by Nasonville Substation | 5000
Total Customers Served by Nasonville Substation | 9670
Switching Plan Completion Time (Hours) | 2
Repair Completion Time (Hours) | 24
| Customers Interrupted (CI) | Customer Minutes Interrupted (CMI) | Circuit Average Interruption Frequency Index (CKAIFI) | Circuit Average Interruption Duration Index (CKAIDI)
Switching Plan Restoration Step | 3456.1554 | 414738.6475 | 0.35741 | 42.8892
Repair Restoration Step | 6213.8446 | 8947936.2302 | 0.64259 | 925.3295
Restoration Event Total | 9670 | 9362674.8777 | 1 | 968.2187

## Annual 24h Outage Add Resources
Inputs and Assumptions
RIE Customers Served by Nasonville Substation | 4670
CREW Customers Served by Nasonville Substation | 5000
Total Customers Served by Nasonville Substation | 9670
Roll-on Generation Capacity (MVA) | 6
Eleanor Slator Hospital Generator Capacity (MVA) | 0.75
CREW Combined Heat and Power Generator Capacity (MVA) | 1.1
CREW Battery Energy Storage System Capacity (MVA) | 3
Switching Plan Completion Time (Hours) | 2
Dispatchable Generation Dispatch Time (Hours) | 2
CREW Battery Energy Storage System Discharge Time (Hours) | 21
Repair Completion Time (Hours) | 24
| Customers Interrupted (CI) | Customer Minutes Interrupted (CMI) | Circuit Average Interruption Frequency Index (CKAIFI) | Circuit Average Interruption Duration Index (CKAIDI)
Switching Plan Restoration Step | 3456.1554 | 414738.6475 | 0.35741 | 42.8892
Dispatchable Generation Restoration Step | 2184.446 | 262133.5252 | 0.2259 | 27.1079
Battery Discharge Restoration Step | 834.8201 | 1051873.3813 | 0.086331 | 108.777
Repair Restoration Step | 3194.5784 | 4600192.9209 | 0.33036 | 475.718
Restoration Event Total | 9670 | 6328938.4748 | 1 | 654.4921